## Coversheet
INSTRUMENT DATASHEET FOR PRESSURE INDICATING TRANSMITTER AND DIFFERENTIAL PRESSURE INDICATING TRANSMITTER
SETTING UP OF STORM WATER GUARD POND, RO - ZLD PLANT, NEW WWTP & AUGMENTATION OF EXISTING WWTP | [5 empty] | Job No. | Unit No. |  | Project | Doc. Code |  | Serial No. | Rev. |  | Page No.
[6 empty] | PC286 | 100 |  | 10P195 | I0003 |  | 118 | 01 |  | 1 of 5
CLIENT |  |  | : |  | GAIL (INDIA) LTD
PMC |  |  | : |  | PROJECT AND DEVELOPMENT INDIA LIMITED
CONTRACTOR |  |  | : |  | VA TECH WABAG LIMITED
DOCUMENT TITLE Instrument Datasheet for New WWTP Pressure & Differential Pressure Transmitter
STAMPING AREA
DOCUMENT CLASS |  |  | : | APPROVAL
DISCIPLINE |  |  | : | INSTRUMENTATION
02 | 12.03.2026 | ISSUED FOR APPROVAL | [5 empty] | AKB |  |  | AG |  |  | VE
01 | 09.02.2026 | ISSUED FOR APPROVAL | [5 empty] | AKB |  |  | AG |  |  | VE
0 | 10.09.2025 | ISSUED FOR APPROVAL | [5 empty] | AKB |  |  | AG |  |  | VE
REV | DATE | DESCRIPTION | [5 empty] | PREPARED BY |  |  | CHECKED BY |  |  | APPROVED BY

## DS PIT (hidden)
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 | [6 empty] | INSTRUMENT DATASHEET FOR PRESSURE INDICATING TRANSMITTER - NEW WWTP
PROJECT | : | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  |  | ISSUED FOR |  |  |  | ENQUIRY
CLIENT | : | GAIL
General Data | 1 | Tag Number |  |  |  |  | Refer Annexure-1
| 2 | Service |  |  |  |  | Refer Annexure-1
| 3 | Type |  |  |  |  | SMART
| 4 | SIL Level Required |  |  |  |  | SIL 2
| 5 | Function |  | Power Supply |  |  | Transmit and Indicate |  |  |  | 24 V DC (2-wire)
| 6 | Mounting |  |  |  |  | 2" pipe mounting
| 7 | Area Classification |  |  |  |  | Refer Annexure-1
| 8 | Enclosure |  | Intrinsic Safety |  |  | IP67 |  |  |  | Yes
| 9 | Cable Entry |  | Accuracy |  |  | 1/2 " NPT(F) |  |  |  | +/- 0.050%
| 10 | Output Type |  | Driving Voltage |  |  | 4-20 mA, 2 wire system |  |  |  | 24 VDC (Loop Powered)
| 11 | Protocol |  |  |  |  | HART Communication protocol
Process Conditions | 12 | Fluid |  |  |  |  | Refer Annexure-1
| 13 | Pressure | Operating |  | Design |  | Refer Annexure-1 |  |  |  | Refer Annexure-1
| 14 | Temperature | Operating |  | Design |  | Refer Annexure-1 |  |  |  | Refer Annexure-1
| 15 | Density |  | Oper.Viscosity |  |  | Refer Annexure-1 |  |  |  | Refer Annexure-1
Measuring Unit | 16 | Inst Range | Min | Max |  | UOM | Refer Annexure-1 |  |  | Refer Annexure-1 |  |  |  | kg/cm2
| 17 | Calibration Range | Min | Max |  | UOM | Refer Annexure-1 |  |  | Refer Annexure-1 |  |  |  | kg/cm2
| 18 | Elevation |  | Suppresion |  |  | NA |  |  |  | NA
| 19 | Element Type |  |  |  |  | Piezoresistive
| 20 | Housing |  |  |  |  | Die-Cast Aluminium Powder Coated
| 21 | Rangeability |  |  |  |  | 1:100
| 22 | Body Material |  |  |  |  | SS
| 23 | Element Material |  | Blow-Out |  |  | SS 316L
| 24 | Over Range Protection |  |  |  |  | Note 10
| 25 | Process Connection |  |  |  |  | 1/2" NPT(F)
| 26 | Connection Location |  |  |  |  | W/o Diaphragm Seal: 1/2" NPT F (Through Manifold) W/Diaphragm Seal: Refer Annexure
Diaphragm Seal (If applicable as per Annexure-1) | 27 | Diaphragm Seal |  |  |  |  | Refer Annexure-1
| 28 | Wetted Part Material |  |  |  |  | SS 316L
| 29 | Other Material |  |  |  |  | NA
| 30 | Process Connection |  |  |  |  | 3" Flanged
| 31 | Size & Rating |  |  |  |  | 3" & Refer Annexure-1
| 32 | Facing & Finish |  |  |  |  | RF
| 33 | Flange Material |  |  |  |  | SS316
| 34 | Flushing/Filling Connection with Plug |  | Capillary Length |  |  | SS316
Options | 35 | Air Filter Regulator |  |  |  |  | NA
| 36 | SPD |  |  |  |  | NA
| 37 | Syphon |  |  |  |  | NA
| 38 | Adjustable Dampner |  |  |  |  | NA
| 39 | Manifold Valve |  |  |  |  | Refer Annexure-1
| 40 | MOC of Manifold Valve |  |  |  |  | SS316L
| 41 | Nameplate |  |  |  |  | SS304
| 42 | Mounting Accessories |  |  |  |  | 2" Pipe Mounting acessories
| 43 | Adapter |  |  |  |  | -
Certification | 44 | Stautory Certification Requirement |  |  |  |  | Zone 2, group IIC, T6, Eexia
| 45 | Calibration Certificate |  |  |  |  | Povided along with transmitter
Purchase | 46 | Requisition Number |  |  |  |  | MBG-PR-82784
| 47 | Manufacturer |  |  |  |  | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser
| 48 | Model |  |  |  |  | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50
| 49 | Purchase Order Number |  |  |  |  | EPC-PO-50473
| 50 | Quantity |  |  |  |  | 3
| 51 | Mandatory Spare Quantity |  |  |  |  | Refer Note 10
Notes: 1.Transmitter should delivering rated current into external load of atleast 600 ohms when powered with 24 V. 2.Local Display should be configurable. 3.Transmitter shall be suitable to Hazardous area classification. 4.The transmitter shall be certified as Ex ia; however, it shall be capable of operating at 24 VDC. 5.NA - NOT APPLICABLE 6.Remote Seal PT/DPT shall be with min 5 mtr Capillary with SS armoured in PVC sheath of Protection with DRIP RING and with SS304 Ball type Isolation Valve 7.For Vessel/Equipment requiring more than 5 m capillary electronic remote seal shall be provided 8.Over Pressure of at least 30% of Instrument range or maximum working pressure whichever is higher. 9.The spare considered shall be 10% of each type of instruments, subject to minimum 2 nos of each type.

## DS NEW WWTP
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 | [6 empty] | INSTRUMENT DATASHEET FOR PRESSURE INDICATING TRANSMITTER - NEW WWTP
PROJECT | : | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  |  | ISSUED FOR APPROVAL
CLIENT | : | GAIL
LOCATION | : | PATA
General Data | 1 | Tag Number |  |  |  |  | Refer Annexure-3
| 2 | Service |  |  |  |  | Refer Annexure-3
| 3 | Type |  |  |  |  | SMART |  |  |  | Pressure Transmitter
| 4 | Function |  | Power Supply |  |  | Transmit and Indicate |  |  |  | 24 V DC (2-wire)
| 5 | Mounting |  | Case |  |  | 2" pipe mounting |  |  |  | Die-Cast Aluminium with Polyster Coated
| 6 | Area Classification |  |  |  |  | Safe Area
| 7 | Enclosure |  | Intrinsic Safety |  |  | IP67 |  |  |  | Yes
| 8 | Cable Entry |  | Accuracy |  |  | 1/2 " NPT(F) |  |  |  | +/- 0.055%
| 9 | Output Type |  | Driving Voltage |  |  | 4-20 mA, 2 wire system |  |  |  | 24 VDC (Loop Powered)
| 10 | Protocol |  |  |  |  | HART Version 7
Process Conditions | 11 | Fluid |  |  |  |  | Refer Annexure-3
| 12 | Pressure | Operating |  | Design |  | Refer Annexure-3 |  |  |  | Refer Annexure-3
| 13 | Temperature | Operating |  | Design |  | Refer Annexure-3 |  |  |  | Refer Annexure-3
| 14 | Density |  | Oper.Viscosity |  |  | Refer Annexure-3 |  |  |  | Refer Annexure-3
Measuring Unit | 15 | Inst Range | Min | Max |  | UOM | Refer Annexure-3 |  |  | Refer Annexure-3 |  |  |  | kg/cm2
| 16 | Calibration Range | Min | Max |  | UOM | Refer Annexure-3 |  |  | Refer Annexure-3 |  |  |  | kg/cm2
| 17 | Elevation |  | Suppresion |  |  | NA |  |  |  | NA
| 18 | Element Type |  |  |  |  | Piezoresistive
| 19 | Housing |  |  |  |  | Die-Cast Aluminium with Polyster Coated
| 20 | Rangeability |  |  |  |  | 1:100
| 21 | Body Material |  |  |  |  | SS
| 22 | Element Material |  | Blow-Out |  |  | SS 316L
| 23 | Over Range Protection |  |  |  |  | Note 10
| 24 | Process Connection |  |  |  |  | 1/2" NPT(F)
| 25 | Connection Location |  |  |  |  | W/o Diaphragm Seal: 1/2" NPT F (Through Manifold) W/Diaphragm Seal: Refer Annexure
Diaphragm Seal (If applicable as per Annexure-1) | 26 | Dial Seal |  | Type |  |  | Refer Annexure-3 |  |  |  |  | VTS
| 27 | Wetted Part Material |  |  |  |  | SS 316L
| 28 | Other Material |  |  |  |  | NA
| 29 | Process Connection |  |  |  |  | 3" Flanged
| 30 | Size & Rating |  |  |  |  | Refer Annexure-1
| 31 | Facing & Finish |  |  |  |  | RF
| 32 | Capillary Material |  | Extension Length |  |  | SS316
| 33 | Capillary Length |  | Rating | Face |  | 5 Meters
| 34 | Armour Type |  |  |  |  | Flexible
| 35 | Armour Material |  |  |  |  | SS304
| 36 | Flange Material |  |  |  |  | SS316
| 37 | Gasket Material |  | Flushing |  |  | VTS
| 38 | Bolt Material |  | Nut Material |  |  | VTS
| 39 | Flushing/Filling Connection with Plug |  | Capillary Length |  |  | SS316
Options | 40 | Air Filter Regulator |  |  |  |  | NA
| 41 | Output Meter (Instrinsically Safe) |  |  |  |  | Yes
| 42 | SPD |  |  |  |  | NA
| 43 | Syphon |  |  |  |  | NA
| 44 | Adjustable Dampner |  |  |  |  | -
| 45 | Manifold Valve |  |  |  |  | Refer Annexure-3
| 46 | MOC of Manifold Valve |  |  |  |  | SS316L
| 47 | Nameplate |  |  |  |  | SS304
| 48 | Mounting Accessories |  |  |  |  | Accessories suitable for 2" Pipe Mounting.Mouting Bracket with Bolts in SS304.
| 49 | Adapter |  |  |  |  | -
| 50 | Square Root Extractor |  |  |  |  | Not used
Certification | 51 | Stautory Certification Requirement |  |  |  |  | ATEX/IEC II 1G Ex ia IIC T4 Ga
| 52 | Calibration Certificate |  |  |  |  | Povided along with transmitter
Purchase | 53 | Requisition Number |  |  |  |  | MBG-PR-82784
| 54 | Manufacturer |  |  |  |  | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser | Endress+Hauser
| 55 | Model |  |  |  |  | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50 | Cerabar PMP50
| 56 | Purchase Order Number |  |  |  |  | EPC-PO-50473
| 57 | Quantity |  |  |  |  | 9
| 58 | Mandatory Spare Quantity |  |  |  |  | Refer Note 11
Notes: 1.Differential pressure transmitters shall be modern inherent motion-free type. 2.Transmitter should delivering rated current into external load of atleast 600 ohms when powered with 24 V. 3.Local Display should be configurable. 4.Transmitter shall be suitable to Hazardous area classification. 5.The transmitter shall be certified as Ex ia; however, it shall be capable of operating at 24 VDC. 6.VTS - VENDOR TO SPECIFY; NA - NOT APPLICABLE 7.Remote Seal PT/DPT shall be with min 5 mtr Capillary with SS armoured in PVC sheath of Protection with DRIP RING and with SS304 Ball type Isolation Valve 8.For Vessel/Equipment requiring more than 5 m capillary electronic remote seal shall be provided 9.DP transmitters with diaphragm seals are envisaged, where condensing leg required to be filled in normal DP transmitters, at all those locations, remote seal type DP transmitters are to be used. Also, wherever there is a control and interlock on level measurement, one transmitter shall be remote diaphragm seal type and one will be guided radar type with Material: Minimum Inconel. 10. Over Pressure of at least 30% of Instrument range or maximum working pressure whichever is higher. 11.The spare considered shall be 10% of each type of instruments, subject to minimum 2 nos of each type.

## Annexure 1- NEW WWTP
INSTRUMENT DATASHEET FOR PRESSURE INDICATING TRANSMITTER-NEW WWTP
ANNEXURE - 1
PROJECT |  | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA | [20 empty] | WABAG DOC NO. | 10P195-I0003-118
CLIENT |  | GAIL | [20 empty] | REV NO. | 02
LOCATION |  | PATA | [20 empty] | DATE | 17.03.2026
S.NO. | TAG NO. | INSTRUMENT TYPE | PROCESS FLUID | LOCATION | P&ID N0. | AREA CLASSIFICATION | LINE/EQUIPMENT. NO. | LINE SIZE(inch) | LINE MOC | RATING | TEMPERATURE IN DEG. C |  | PRESSURE (Kg/cm2) |  |  | CALIBRATION RANGE | INSTRUMENT RANGE | UNIT OF MEASUREMENT | TYPE | FLUSHING RING | MANIFOLD | PROCESS TAPPING END CONNECTION | MODEL NUMBER | REMARKS
[11 empty] | NOR. | MAX | MIN | NOR | MAX
1 | 100-PIT-10102 | PRESSURE INDICATING TRANSMITTER | PROCESS AIR | FROM EXISTING MRS - I (OWS - PC II) | 10P195-D0015-101 | Safe Area | 4"-OWS-10104-B24-NI | 4" | CARBON STEEL | #150 | AMB | AMB | 0 | 6.5 | 10 | 0-15 | 0-40 | (Kg/cm2) | WITH DIAPHRAGM SEAL | NA | 2 way T type SS316 manifold | 1/2" NPTF |  | NEWLY ADDED
2 | 100-PIT-10104 | PRESSURE INDICATING TRANSMITTER | INSTRUMENT AIR | FROM PLANT AIR | 10P195-D0015-101 | Safe Area | 1"-PA-10104-B24-NI | 1" | CARBON STEEL | #150 | AMB | AMB | 0 | 6.5 | 10 | 0-15 | 0-40 | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL | NA | 2 way T type SS316 manifold | 1/2" NPTF | PMP50-BABACJH6AA3SJA1VWJA1+FANPQ1Z1
3 | 100-PIT-14602 | PRESSURE INDICATING TRANSMITTER | AIR | OUTLET OF VOC AIR BLOWER 100-BL-003 | 10P195-D0015-146 | Safe Area | 12"-VA-14608-B24-NI | 12" | CARBON STEEL | #150 | 42 | 90 | 0 | 1.16 | 3 | 0-5 | 0-10 | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL | NA | 2 way T type SS316 manifold | 1/2" NPTF | PMP50-BABACJH6AA3PJA1VWJA1FAQ1Z1
4 | 100-PIT-10101 | PRESSURE INDICATING TRANSMITTER | CLARIFIED RAIN WATER SEWAGE | FROM EXISTING MRS - I (CRWS) TO CRWS BUFFER TANK | 10P195-D0015-101 | Safe Area | 14"-CRWS-10113-B24-NI | 14" | CARBON STEEL | #150 | 30 | 35 | 0 | 4 | 4 | 0-5 | 0-10 | (Kg/cm2) | WITH DIAPHRAGM SEAL |  |  |  |  | NEWLY ADDED
5 | 100-PIT-10103 | PRESSURE INDICATING TRANSMITTER | OILY WATER STREAM | FROM EXISTING MRS-I PUMPS | 10P195-D0015-101 | Safe Area | 12"-OWS-40201-B24-NI | 12" | CARBON STEEL | #150 | 30 | 35 | 0 | 2 | 3 | 0-5 | 0-10 | (Kg/cm2) | WITH DIAPHRAGM SEAL |  |  |  |  | NEWLY ADDED
6 | 100-PIT-10105 | PRESSURE INDICATING TRANSMITTER | INSTRUMENT AIR | FROM INSTRUMENT AIR HEADER | 10P195-D0015-101 | Safe Area | 1 1/2"-IA-10105-B50-NI | 1 1/2" | SS304/SS304L- STAINLESS STEEL | #150 | [7 empty] | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL
7 | 100-PIT-10106 | PRESSURE INDICATING TRANSMITTER | INSTRUMENT AIR | FROM SERVICE WATER HEADER | 10P195-D0015-101 | Safe Area | 3"-SW-10107-B24-NI | 3" | CARBON STEEL | #150 | 30 | 35 | 0 | 3.5 | 4.5 |  |  | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL |  |  |  |  | NEWLY ADDED
8 | 100-PIT-10107 | PRESSURE INDICATING TRANSMITTER | DRINKING WATER | FROM DRINKING WATER HEADER | 10P195-D0015-101 | Safe Area | 2"-DW-10109-B22G-NI | 2" | GALVANIZED STEEL | #150 | [7 empty] | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL |  |  |  |  | NEWLY ADDED
9 | 100-PIT-10202 | PRESSURE INDICATING TRANSMITTER | NITROGEN | FROM NITROGEN HEADER | 10P195-D0015-102 | Safe Area | 2"-NI-10202-B24-NI | 2" | CARBON STEEL | #150 | [7 empty] | (Kg/cm2) | WITHOUT DIAPHRAGM SEAL |  |  |  |  | NEWLY ADDED

## DS AUGG WWTP (hidden)
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 | [6 empty] | INSTRUMENT DATASHEET FOR PRESSURE INDICATING TRANSMITTER - AUGG WWTP
PROJECT | : | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  |  | ISSUED FOR |  |  | ENQUIRY
CLIENT | : | PDIL GAIL
LOCATION | : | PATA
General Data | 1 | Tag Number |  |  |  |  | Refer Annexure-2
| 2 | Service |  |  |  |  | Refer Annexure-2
| 3 | Type |  |  |  |  | SMART |  | Differential pressure Transmitter
| 4 | Function |  | Power Supply |  |  | Transmit and Indicate |  | 24 V DC (2-wire)
| 5 | Mounting |  | Case |  |  | 2" pipe mounting |  | Diecast Aluminum with PU coating
| 6 | Area Classification |  |  |  |  | Safe Area
| 7 | Enclosure |  | Intrinsic Safety |  |  | IP67 |  | Yes
| 8 | Cable Entry |  | Accuracy |  |  | 1/2 " NPT(F) |  | +/- 0.050%
| 9 | Output Type |  | Driving Voltage |  |  | 4-20 mA, 2 wire system |  | 24 VDC (Loop Powered)
| 10 | Protocol |  |  |  |  | HART Communication protocol(HART-7)
Process Conditions | 11 | Fluid |  |  |  |  | Refer Annexure-2
| 12 | Pressure | Operating |  | Design |  | Refer Annexure-2 |  | Refer Annexure-2
| 13 | Temperature | Operating |  | Design |  | Refer Annexure-2 |  | Refer Annexure-2
| 14 | Density |  | Oper.Viscosity |  |  | Refer Annexure-2 |  | Refer Annexure-2
Measuring Unit | 15 | Inst Range | Min | Max |  | UOM | Refer Annexure-2 | Refer Annexure-2 |  |  | kg/cm2
| 16 | Calibration Range | Min | Max |  | UOM | Refer Annexure-2 | Refer Annexure-2 |  |  | kg/cm2
| 17 | Elevation |  | Suppresion |  |  | NA |  | NA
| 18 | Element Type |  |  |  |  | VTS
| 19 | Housing |  |  |  |  | Die-Cast Aluminium .Epoxy Painted
| 20 | Rangeability |  |  |  |  | 1:100
| 21 | Body Material |  |  |  |  | SS
| 22 | Element Material |  | Blow-Out |  |  | SS 316L
| 23 | Over Range Protection |  |  |  |  | Note 10
| 24 | Process Connection |  |  |  |  | 1/2" NPT(F)
| 25 | Connection Location |  |  |  |  | W/o Diaphragm Seal: 1/2" NPT F (Through Manifold) W/Diaphragm Seal: Refer Annexure
Diaphragm Seal (If applicable as per Annexure-1) | 26 | Dial Seal |  | Type |  |  | NA |  |  | NA
| 27 | Wetted Part Material |  |  |  |  | NA
| 28 | Other Material |  |  |  |  | NA
| 29 | Process Connection |  |  |  |  | NA
| 30 | Size & Rating |  |  |  |  | NA
| 31 | Facing & Finish |  |  |  |  | NA
| 32 | Capillary Material |  | Extension Length |  |  | NA
| 33 | Capillary Length |  | Rating | Face |  | NA
| 34 | Armour Type |  |  |  |  | NA |  |  |  |  | vts
| 35 | Armour Material |  |  |  |  | NA |  |  |  |  | vts
| 36 | Flange Material |  |  |  |  | NA
| 37 | Gasket Material |  | Flushing |  |  | NA
| 38 | Bolt Material |  | Nut Material |  |  | NA
| 39 | Flushing/Filling Connection with Plug |  | Capillary Length |  |  | NA
Options | 40 | Air Filter Regulator |  |  |  |  | NA
| 41 | Output Meter (Instrinsically Safe) |  |  |  |  | Yes
| 42 | SPD |  |  |  |  | NA
| 43 | Syphon |  |  |  |  | VTS
| 44 | Adjustable Dampner |  |  |  |  | -
| 45 | Manifold Valve |  |  |  |  | Refer Annexure-2
| 46 | MOC of Manifold Valve |  |  |  |  | SS316L
| 47 | Nameplate |  |  |  |  | SS304
| 48 | Mounting Accessories |  |  |  |  | Accessories suitable for 2" Pipe Mounting.Mouting Bracket with Bolts in SS304.
| 49 | Adapter |  |  |  |  | -
| 50 | Square Root Extractor |  |  |  |  | Not used
Certification | 51 | Stautory Certification Requirement |  |  |  |  | Zone 2, group IIC, T6, Eexia
| 52 | Calibration Certificate |  |  |  |  | Povided along with transmitter
Purchase | 53 | Requisition Number |  |  |  |  | TBA
| 54 | Manufacturer |  |  |  |  | VTS
| 55 | Model |  |  |  |  | VTS
| 56 | Purchase Order Number |  |  |  |  | TBA
| 57 | Quantity |  |  |  |  | 1
| 58 | Mandatory Spare Quantity |  |  |  |  | TBA
Notes: 1.Differential pressure transmitters shall be modern inherent motion-free type. 2.Transmitter should delivering rated current into external load of atleast 600 ohms when powered with 24 V. 3.Local Display should be configurable. 4.Transmitter shall be suitable to Hazardous area classification. 5.The transmitter shall be certified as Ex ia; however, it shall be capable of operating at 24 VDC. 6.VTS - VENDOR TO SPECIFY; NA - NOT APPLICABLE 7.Remote Seal PT/DPT shall be with min 5 mtr Capillary with SS armoured in PVC sheath of Protection with DRIP RING and with SS304 Ball type Isolation Valve 8.For Vessel/Equipment requiring more than 5 m capillary electronic remote seal shall be provided 9.DP transmitters with diaphragm seals are envisaged, where condensing leg required to be filled in normal DP transmitters, at all those locations, remote seal type DP transmitters are to be used. Also, wherever there is a control and interlock on level measurement, one transmitter shall be remote diaphragm seal type and one will be guided radar type with Material: Minimum Inconel. 10. Over Pressure of at least 30% of Instrument range or maximum working pressure whichever is higher.