## Coversheet
INSTRUMENT DATASHEET FOR PRESSURE INDICATOR
SETTING UP OF STORM WATER GUARD POND, RO - ZLD PLANT, NEW WWTP & AUGMENTATION OF EXISTING WWTP | [5 empty] | Job No. | Unit No. |  | Project | Doc. Code |  | Serial No. | Rev. |  | Page No.
[6 empty] | PC286 | 200 |  | 10P195 | I0003 |  | 208 | 01 |  | 1 of 5
CLIENT |  |  | : |  | GAIL (INDIA) LTD
PMC |  |  | : |  | PROJECT AND DEVELOPMENT INDIA LIMITED
CONTRACTOR |  |  | : |  | VA TECH WABAG LIMITED
DOCUMENT TITLE Instrument Datasheet for Storm Water Guard Pond Pressure Indicator-Bourdon Type
STAMPING AREA
DOCUMENT CLASS |  |  | : | APPROVAL
DISCIPLINE |  |  | : | INSTRUMENTATION
01 | 11.03.2026 | ISSUED FOR APPROVAL | [5 empty] | AKB |  |  | AG |  |  | VE
00 | 10.12.2025 | ISSUED FOR APPROVAL | [5 empty] | AKB |  |  | AG |  |  | VE
REV | DATE | DESCRIPTION | [5 empty] | PREPARED BY |  |  | CHECKED BY |  |  | APPROVED BY

## DS PG
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 |  |  |  |  | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - BOURDON TYPE
PROJECT | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  | ISSUED FOR |  |  | ENQUIRY
CLIENT | GAIL
LOCATION | PATA
GENERAL | Tag No |  |  |  | REFER ANNEXURE-1
| P&ID No |  |  |  | REFER ANNEXURE-1
| Location |  |  |  | REFER ANNEXURE-1
| Line No. |  |  |  | REFER ANNEXURE-1
PROCESS CONDITIONS | Fluid |  |  |  | REFER ANNEXURE-1
| Specific Gravity |  |  |  | REFER ANNEXURE-1
| Viscosity(Centipoise) |  |  |  | REFER ANNEXURE-1
| Flow(m3/hr) | Min. | Nor. | Max. | REFER ANNEXURE-1 |  | REFER ANNEXURE-1 |  | REFER ANNEXURE-1
| Pressure (Kg/cm2 g) | Min. | Nor. | Max. | REFER ANNEXURE-1 |  | REFER ANNEXURE-1 |  | REFER ANNEXURE-1
| Temp(°C) | Min. | Nor. | Max. | REFER ANNEXURE-1 |  | REFER ANNEXURE-1 |  | REFER ANNEXURE-1
SENSOR | Instrument Type |  |  |  | REFER ANNEXURE-1
| Instrument Range |  | Instrument Range |  | REFER ANNEXURE-1
| Mounting |  | Mounting |  | LOCAL
| Dial Size |  | Dial Size |  | 150mm
| Dial Material |  | Dial Material |  | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum
| Dial Fill Fluid |  | Dial Fill Fluid |  | Glycerin | Glycerin | Glycerin | Glycerin | Glycerin | Glycerin
| Dial Color |  | Dial Color |  | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals
| Case |  | Case |  | SS316L
| Bezel Ring |  | Bezel Ring |  | Bayonet Type
| Pressure Element Type |  | Pressure Element Type |  | REFER ANNEXURE-1
| Pressure Element Material |  | Pressure Element Material |  | SS316L
| Socket Material |  | Socket Material |  | SS316L
| Connection Size |  | Connection Size |  | REFER ANNEXURE-1
| Connection Location |  | Connection Location |  | BOTTOM
| Movement Material |  | Movement Material |  | SS304
| Accuracy |  | Accuracy |  | ± 1 % of full scale
| Enclosure Protection Class |  | Enclosure Protection Class |  | IP 66
| Over Range Protection |  | Over Range Protection |  | 110% for flange type gauges 130% for bourdon type gauges
| Blow - Out Protection |  | Blow - Out Protection |  | Refer Note-4
| Window Material |  | Window Material |  | SHATTER PROOF GLASS
| Zero Adjustment |  | Zero Adjustment |  | REQUIRED
DIAPHRAGM SEAL | Process Connection |  |  |  | NA
| Diaphragm Material |  | Diaphragm Material |  | NA
| Bottom Flange Material |  | Bottom Flange Material |  | NA
| Fill Fluid |  | Fill Fluid |  | NA
| Capillary Length |  | Capillary Length |  | NA
| Capillary Material |  | Capillary Material |  | NA
| Top Flange Material |  | Top Flange Material |  | NA
| Flushing Connection |  |  |  | NA
| Wetted Part Material |  |  |  | NA
OPTIONS | Mounting Accessories |  |  |  | Required only for remote mounting
| Manifold |  |  |  | Two valve integral manifold
| MOC of Manifold |  |  |  | SS316L
| Pulsation Dampener |  |  |  | Refer Note-2
| Liquid Filled Casing |  |  |  | Refer Note-6
| Syphon Type |  |  |  | Pig Tail Syphon considered only for steam service
| Syphon Material |  |  |  | SS316
| Stop Pin |  |  |  | REQUIRED
| SS Tag Plate |  |  |  | REQUIRED
CERTIFICATION | Calibration Certificate |  |  |  | REQUIRED
| ATEX Certification |  |  |  | -
PURCHASE | Make |  |  |  | WALCHANDNAGAR INDUSTRIES LIMITED
| Model |  |  |  | PQS-SSSSEXGF150-11+2VM
| Qty |  |  |  | 25
| Maintenance Spares |  |  |  | Provided
| Commisioning Spares |  |  |  | Later
Notes:
1.The gauge for 60 kg/cm2 above pressure shall preferably be a safety type with solid front where pointer and glass are partitioned off from the sensor by a solid disc
2.Pulsation dampeners shall be installed with the gauges where pulsating pressure occurs
3.Blow-out discs are required for all pressure gauges except for instrument air services
4.Vibration proof gauges or remote seal type shall be used if the surrounding environment is subject to vibration
5.Pressure gauges for vibrating services(pump discharge) shall be glycerine filled type or with pulsating dampener device and Sealing liquid must be selected as per process requirement
6. NA - Not Applicable TBC - To Be Confirmed

## Annexure-1 SWGP
INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - STROM WATER GUARD POND
ANNEXURE - 1
PROJECT |  | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA | [13 empty] | WABAG DOC NO. |  | 10P195-I0003-208
CLIENT |  | GAIL | [13 empty] | REV NO. |  | 01
LOCATION |  | PATA | [13 empty] | DATE |  | 11.03.2026
S.NO. | TAG NO. | INSTRUMENT TYPE | PROCESS FLUID | LOCATION | P&ID N0. | LINE/EQUIPMENT. NO. | LINE SIZE | LINE MOC WITH RATING | DESIGN TEMPERATURE °C | PRESSURE (Kg/cm2) |  |  | PROCESS CONNECTION | FLUSHING RING | INSTRUMENT RANGE | UNIT OF MEASUREMENT | MAKE | MODEL NUMBER | REMARKS
[7 empty] | LINE SIZE |  |  | MIN | NOR | MAX
1 | 200-PG-20501 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | OUTLET OF FILTER FEED PUMP A - 200-PM-002 A | 10P195-D0015-205 | 6"-WS-20501-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 3.5 | 1/2" NPT(M) | NA | 0 to 5 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
2 | 200-PG-20502 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | OUTLET OF FILTER FEED PUMP B- 200-PM-002 B | 10P195-D0015-205 | 6"-WS-20502-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 3.5 | 1/2" NPT(M) | NA | 0 to 5 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
3 | 200-PG-20503 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | OUTLET OF FILTER FEED PUMP C- 200-PM-002 C | 10P195-D0015-205 | 6"-WS-20503-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 3.5 | 1/2" NPT(M) | NA | 0 to 5 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
4 | 200-PG-20504 | PRESSURE GAUGE- BOURDON TYPE | BACKWASH | OUTLET OF STORM WATER FILTER BACKWASH PUMP A - 200-PM-003 A | 10P195-D0015-205 | 14"-BW-20505-B24-NI | 14" | CARBON STEEL,150# | 65 | 0 | 2 | 3.5 | 1/2" NPT(M) | NA | 0 to 5 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
5 | 200-PG-20505 | PRESSURE GAUGE- BOURDON TYPE | BACKWASH | OUTLET OF STORM WATER FILTER BACKWASH PUMP B - 200-PM-003 B | 10P195-D0015-205 | 14"-BW-20506-B24-NI | 14" | CARBON STEEL,150# | 65 | 0 | 2 | 3.5 | 1/2" NPT(M) | NA | 0 to 5 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
6 | 200-PG-20701 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | INLET OF DUAL MEDIA FILTER 200-V-001 A | 10P195-D0015-207 | 6"-WS-20601-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
7 | 200-PG-20702 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | OUTLET OF DUAL MEDIA FILTER 200-V-001 A | 10P195-D0015-207 | 6"-WF-20702-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
8 | 200-PG-20703 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | OUTLET OF DUAL MEDIA FILTER 200-V-001 A | 10P195-D0015-207 | 6"-WF-20702-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
9 | 200-PG-20801 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | INLET OF DUAL MEDIA FILTER 200-V-001 B | 10P195-D0015-208 | 6"-WS-20602-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
10 | 200-PG-20802 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | OUTLET OF DUAL MEDIA FILTER 200-V-001 B | 10P195-D0015-208 | 6"-WF-20805-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
11 | 200-PG-20803 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | OUTLET OF DUAL MEDIA FILTER 200-V-001 B | 10P195-D0015-208 | 6"-WF-20805-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
12 | 200-PG-20901 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | INLET OF DUAL MEDIA FILTER 200-V-001 C | 10P195-D0015-209 | 6"-WS-20603-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.5 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
13 | 200-PG-20902 | PRESSURE GAUGE- BOURDON TYPE | STORM WATER | DUAL MEDIA FILTER 200-V-001 C | 10P195-D0015-209 | 6"-WF-20905-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
14 | 200-PG-20903 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | OUTLET OF DUAL MEDIA FILTER 200-V-001 C | 10P195-D0015-209 | 6"-WF-20905-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
15 | 200-PG-21101 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | INLET OF ACTIVATED CARBON FILTER A - 200-V-002 A | 10P195-D0015-211 | 6"-WF-21001-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
16 | 200-PG-21102 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OFACTIVATED CARBON FILTER A - 200-V-002 A | 10P195-D0015-211 | 6"-TW-21105-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.1 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
17 | 200-PG-21103 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OFACTIVATED CARBON FILTER A - 200-V-002 A | 10P195-D0015-211 | 6"-TW-21105-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
18 | 200-PG-21201 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | INLET OF ACTIVATED CARBON FILTER A - 200-V-002 B | 10P195-D0015-212 | 6"-WF-21002-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
19 | 200-PG-21202 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OFACTIVATED CARBON FILTER A - 200-V-002 B | 10P195-D0015-212 | 6"-TW-21205-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.1 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
20 | 200-PG-21203 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OFACTIVATED CARBON FILTER A - 200-V-002 B | 10P195-D0015-212 | 6"-TW-21205-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
21 | 200-PG-21301 | PRESSURE GAUGE- BOURDON TYPE | FILTERED WATER | INLET OF ACTIVATED CARBON FILTER A - 200-V-002 C | 10P195-D0015-213 | 6"-WF-21003-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.3 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
22 | 200-PG-21302 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OF ACTIVATED CARBON FILTER A - 200-V-002 C | 10P195-D0015-213 | 6"-TW-21305-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 3.1 | 4 | 1/2" NPT(M) | NA | 0 to 6 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
23 | 200-PG-21303 | PRESSURE GAUGE- BOURDON TYPE | TREATED WATER | OUTLET OF ACTIVATED CARBON FILTER A - 200-V-002 C | 10P195-D0015-213 | 6"-TW-21305-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 1.5 | 2 | 1/2" NPT(M) | NA | 0 to 3 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
24 | 200-PG-21403 | PRESSURE GAUGE- BOURDON TYPE | PROCESS AIR | OUTLET OF FILTER BACKWASH BLOWER 200-BL-001 A | 10P195-D0015-214 | 6"-PA-21401-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 0.4 | 0.6 | 1/2" NPT(M) | NA | 0 to 1 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM
25 | 200-PG-21404 | PRESSURE GAUGE- BOURDON TYPE | PROCESS AIR | OUTLET OF FILTER BACKWASH BLOWER 200-BL-001 B | 10P195-D0015-214 | 6"-PA-21402-B24-NI | 6" | CARBON STEEL,150# | 65 | 0 | 0.4 | 0.6 | 1/2" NPT(M) | NA | 0 to 1 | Kg/cm2.g | WIL | PQS-SSSSEXGF150-11+2VM

## DS PG-with diaphragm seal
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 |  |  |  |  | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - BOURDON TYPE WITH DIAPHRAGM SEAL
PROJECT | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  | ISSUED FOR |  |  | ENQUIRY
CLIENT | GAIL
LOCATION | PATA
GENERAL | Tag No |  |  |  | REFER ANNEXURE-2
| P&ID No |  |  |  | REFER ANNEXURE-2
| Location |  |  |  | REFER ANNEXURE-2
| Line No. |  |  |  | REFER ANNEXURE-2
PROCESS CONDITIONS | Fluid |  |  |  | REFER ANNEXURE-2
| Specific Gravity |  |  |  | REFER ANNEXURE-2
| Viscosity(Centipoise) |  |  |  | REFER ANNEXURE-2
| Flow(m3/hr) | Min. | Nor. | Max. | REFER ANNEXURE-2 |  | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
| Pressure (Kg/cm2 g) | Min. | Nor. | Max. | REFER ANNEXURE-2 |  | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
| Temp(°C) | Min. | Nor. | Max. | REFER ANNEXURE-2 |  | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
SENSOR | Instrument Type |  |  |  | REFER ANNEXURE-2
| Instrument Range |  | Instrument Range |  | REFER ANNEXURE-2
| Mounting |  | Mounting |  | LOCAL
| Dial Size |  | Dial Size |  | 150mm
| Dial Material |  | Dial Material |  | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum
| Dial Fill Fluid |  | Dial Fill Fluid |  | Glycerin | Glycerin | Glycerin | Glycerin | Glycerin | Glycerin
| Dial Color |  | Dial Color |  | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals | White painted with black numerals
| Case |  | Case |  | SS316L
| Bezel Ring |  | Bezel Ring |  | Bayonet Type
| Pressure Element Type |  | Pressure Element Type |  | REFER ANNEXURE-2
| Pressure Element Material |  | Pressure Element Material |  | SS316L
| Socket Material |  | Socket Material |  | SS316L
| Connection Size |  | Connection Size |  | REFER ANNEXURE-2
| Connection Location |  | Connection Location |  | BOTTOM
| Movement Material |  | Movement Material |  | SS304
| Accuracy |  | Accuracy |  | ± 1 % of full scale
| Enclosure Protection Class |  | Enclosure Protection Class |  | IP 66
| Over Range Protection |  | Over Range Protection |  | 110% for flange type gauges 130% for bourdon type gauges
| Blow - Out Protection |  | Blow - Out Protection |  | Refer Note-4
| Window Material |  | Window Material |  | SHATTER PROOF GLASS
| Zero Adjustment |  | Zero Adjustment |  | REQUIRED
DIAPHRAGM SEAL | Process Connection |  |  |  | REFER ANNEXURE-2
| Diaphragm Material |  | Diaphragm Material |  | Min SS316L
| Bottom Flange Material |  | Bottom Flange Material |  | NA
| Fill Fluid |  | Fill Fluid |  | Silicon Oil
| Capillary Length |  | Capillary Length |  | NA (Refer Note-6)
| Capillary Material |  | Capillary Material |  | NA (Refer Note-6)
| Top Flange Material |  | Top Flange Material |  | SS316L
| Flushing Connection |  |  |  | To be provided by Vendor with Ball Isolation valve
| Wetted Part Material |  |  |  | SS316L
OPTIONS | Mounting Accessories |  |  |  | Required only for remote mounting
| Manifold |  |  |  | Two valve integral manifold
| MOC of Manifold |  |  |  | SS316L
| Pulsation Dampener |  |  |  | Refer Note-2
| Liquid Filled Casing |  |  |  | Refer Note-6
| Syphon Type |  |  |  | Pig Tail Syphon considered only for steam service
| Syphon Material |  |  |  | SS316
| Stop Pin |  |  |  | REQUIRED
| SS Tag Plate |  |  |  | REQUIRED
CERTIFICATION | Calibration Certificate |  |  |  | REQUIRED
| ATEX Certification |  |  |  | -
PURCHASE | Make |  |  |  | TBC
| Model |  |  |  | TBC
| Qty |  |  |  | 6
| Maintenance Spares |  |  |  | Provided
| Commisioning Spares |  |  |  | Later
Notes:
1.The gauge for 60 kg/cm2 above pressure shall preferably be a safety type with solid front where pointer and glass are partitioned off from the sensor by a solid disc
2.Pulsation dampeners shall be installed with the gauges where pulsating pressure occurs
3.Blow-out discs are required for all pressure gauges except for instrument air services
4.Vibration proof gauges or remote seal type shall be used if the surrounding environment is subject to vibration
5.Pressure gauges for vibrating services (pump discharge) shall be glycerine filled type or with pulsating dampener device and Sealing liquid must be selected as per process requirement
6. Capillary type is not used for Pressure indicator with diaphragm seal
7. NA - Not Applicable TBC - To Be Confirmed

## Annexure-2 SWGP
INSTRUMENT DATASHEET FOR PRESSURE INDICATOR WITH DIAPHRAGM SEAL- STORM WATER GUARD POND
ANNEXURE - 2
PROJECT |  | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA | [13 empty] | WABAG DOC NO. |  | 10P195-I0003-208
CLIENT |  | GAIL | [13 empty] | REV NO. |  | 01
LOCATION |  | PATA | [13 empty] | DATE |  | 11.03.2026
S.NO. | TAG NO. | INSTRUMENT TYPE | PROCESS FLUID | LOCATION | P&ID N0. | LINE/EQUIPMENT. NO. | LINE SIZE | LINE MOC WITH RATING | DESIGN TEMPERATURE °C | PRESSURE (Kg/cm2) |  |  | PROCESS CONNECTION | FLUSHING RING | INSTRUMENT RANGE | UNIT OF MEASUREMENT | MAKE | MODEL NUMBER | REMARKS
[10 empty] | MIN | NOR | MAX
1 | 200-PG-20201 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | STORM WATER | OUTLET OF TPI FEED PUMP B - 200-PM-001 A | 10P195-D0015-202 | 10"-WS-20201-B24-NI | 10" | CARBON STEEL,150# | 65 | 0 | 1 | 1.2 | 3" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC
2 | 200-PG-20202 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | STORM WATER | OUTLET OF TPI FEED PUMP B - 200-PM-001 B | 10P195-D0015-202 | 10"-WS-20202-B24-NI | 10" | CARBON STEEL,150# | 65 | 0 | 1 | 1.2 | 3" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC
3 | 200-PG-21503 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | SLUDGE | OUTLET OF TPI SLUDGE PUMP 200-P-004 A | 10P195-D0015-215 | 3"-SL-21503-B24-NI | 3" | CARBON STEEL,150# | 65 | 0 | 2 | 2.5 | 3" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC
4 | 200-PG-21504 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | SLUDGE | OUTLET OF TPI SLUDGE PUMP 200-P-004 B | 10P195-D0015-215 | 3"-SL-21504-B24-NI | 3" | CARBON STEEL,150# | 65 | 0 | 2 | 2.5 | 3" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC
5 | 200-PG-21603 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | SLOP OIL | OUTLET OF TPI OIL PUMP 200-PA-005 A | 10P195-D0015-216 | 1 1/2"-SO-210603-B24-NI | 1 1/2" | CARBON STEEL,150# | 65 | 0 | 2 | 2.5 | 1 1/2" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC
6 | 200-PG-21604 | PRESSURE INDICATOR - WITH DIAPHRAGM SEAL | SLOP OIL | OUTLET OF TPI OIL PUMP 200-PA-005 B | 10P195-D0015-216 | 1 1/2"-SO-210604-B24-NI | 1 1/2" | CARBON STEEL,150# | 65 | 0 | 2 | 2.5 | 1 1/2" FLANGED | Provided by Vendor | TBC | Kg/cm2.g | TBC | TBC

## DS_STROM WATER (hidden)
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 |  |  |  |  | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - BOURDON TYPE
PROJECT | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  | ISSUED FOR |  | ENQUIRY
CLIENT | GAIL
LOCATION | PATA
GENERAL | Tag No |  |  |  | REFER ANNEXURE-2
| P&ID No |  |  |  | REFER ANNEXURE-2
| Location |  |  |  | REFER ANNEXURE-2
| Line No. |  |  |  | REFER ANNEXURE-2
| Area Classification |  |  |  | Safe Area
PROCESS CONDITIONS | Fluid |  |  |  | REFER ANNEXURE-2
| Specific Gravity |  |  |  | REFER ANNEXURE-2
| Viscosity(Centipoise) |  |  |  | REFER ANNEXURE-2
| Flow(m3/hr) | Min. | Nor. | Max. | REFER ANNEXURE-2 | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
| Pressure (Kg/cm2 g) | Min. | Nor. | Max. | REFER ANNEXURE-2 | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
| Temp(°C) | Min. | Nor. | Max. | REFER ANNEXURE-2 | REFER ANNEXURE-2 |  | REFER ANNEXURE-2
SENSOR | Instrument Type |  |  |  | REFER ANNEXURE-2
| Instrument Range |  | Instrument Range |  | REFER ANNEXURE-2
| Mounting |  | Mounting |  | LOCAL
| Dial Size |  | Dial Size |  | 150mm
| Dial Material |  | Dial Material |  | VTS
| Dial Fill Fluid |  | Dial Fill Fluid |  | VTS
| Dial Color |  | Dial Color |  | VTS
| Case |  | Case |  | SS316L
| Bezel Ring |  | Bezel Ring |  | Bayonet Type( Note 3)
| Pressure Element Type |  | Pressure Element Type |  | REFER ANNEXURE-2
| Pressure Element Material |  | Pressure Element Material |  | SS316L
| Socket Material |  | Socket Material |  | VTS
| Connection Size |  | Connection Size |  | REFER ANNEXURE-2
| Connection Location |  | Connection Location |  | BOTTOM
| Movement Material |  | Movement Material |  | VTS
| Accuracy |  | Accuracy |  | ± 1 % of full scale
| Enclosure Protection Class |  | Enclosure Protection Class |  | IP 55
| Over Range Protection |  | Over Range Protection |  | VTS
| Blow - Out Protection |  | Blow - Out Protection |  | Refer Note-4
| Window Material |  | Window Material |  | SHATTER PROOF GLASS
| Zero Adjustment |  | Zero Adjustment |  | EXTERNAL - REQUIRED
DIAPHRAGM SEAL | Process Connection |  |  |  | REFER ANNEXURE-2
| Diaphragm Material |  | Diaphragm Material |  | Min SS316L
| Bottom Flange Material |  | Bottom Flange Material |  | NA
| Fill Fluid |  | Fill Fluid |  | VTS
| Capillary Length |  | Capillary Length |  | NA
| Capillary Material |  | Capillary Material |  | NA
| Top Flange Material |  | Top Flange Material |  | SS316L
| Flushing Connection |  |  |  | To be provided by Vendor
Wetted Part Material
OPTIONS | Mounting Accessories |  |  |  | REQUIRED
| Pulsation Dampener |  |  |  | Refer Note-2
| Liquid Filled Casing |  |  |  | Refer Note-6
| Syphon Type |  |  |  | VTS
| Syphon Material |  |  |  | VTS
| Stop Pin |  |  |  | REQUIRED
| SS Tag Plate |  |  |  | REQUIRED
CERTIFICATION | Calibration Certificate |  |  |  | REQUIRED
| ATEX Certification |  |  |  | -
PURCHASE | Make |  |  |  | VTS
| Model |  |  |  | VTS
| Qty |  |  |  | 35
| Maintenance Spares |  |  |  | TBA
| Commisioning Spares |  |  |  | VTS
Notes:
1.The gauge for 60 kg/cm2 above pressure shall preferably be a safety type with solid front where pointer and glass are partitioned off from the sensor by a solid disc
2.Pulsation dampeners shall be installed with the gauges where pulsating pressure occurs
3.Bezel rings shall be screw on pattern
4.Blow-out discs are required for all pressure gauges except for instrument air services
5.Vibration proof gauges or remote seal type shall be used if the surrounding environment is subject to vibration
6.Pressure gauges for vibrating services(pump discharge) shall be glycerine filled type or with pulsating dampener device and Sealing liquid must be selected as per process requirement
7.Inbuilt snubber will be provided for diaphragm seal type pressure gauge
8.NA - Not Applicable
VTS- Vendor To Specify

## DS_NEW WWTP (hidden)
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 |  |  |  |  | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - BOURDON TYPE
PROJECT | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  | ISSUED FOR |  | ENQUIRY
CLIENT | GAIL
LOCATION | PATA
GENERAL | Tag No |  |  |  | REFER ANNEXURE-3
| P&ID No |  |  |  | REFER ANNEXURE-3
| Location |  |  |  | REFER ANNEXURE-3
| Line No. |  |  |  | REFER ANNEXURE-3
| Area Classification |  |  |  | Safe Area
PROCESS CONDITIONS | Fluid |  |  |  | REFER ANNEXURE-3
| Specific Gravity |  |  |  | REFER ANNEXURE-3
| Viscosity(Centipoise) |  |  |  | REFER ANNEXURE-3
| Flow(m3/hr) | Min. | Nor. | Max. | REFER ANNEXURE-3 | REFER ANNEXURE-3 |  | REFER ANNEXURE-3
| Pressure (Kg/cm2 g) | Min. | Nor. | Max. | REFER ANNEXURE-3 | REFER ANNEXURE-3 |  | REFER ANNEXURE-3
| Temp(°C) | Min. | Nor. | Max. | REFER ANNEXURE-3 | REFER ANNEXURE-3 |  | REFER ANNEXURE-3
SENSOR | Instrument Type |  |  |  | REFER ANNEXURE-3
| Instrument Range |  | Instrument Range |  | REFER ANNEXURE-3
| Mounting |  | Mounting |  | LOCAL
| Dial Size |  | Dial Size |  | 150mm
| Dial Material |  | Dial Material |  | VTS
| Dial Fill Fluid |  | Dial Fill Fluid |  | VTS
| Dial Color |  | Dial Color |  | VTS
| Case |  | Case |  | SS316L
| Bezel Ring |  | Bezel Ring |  | Bayonet Type( Note 3)
| Pressure Element Type |  | Pressure Element Type |  | REFER ANNEXURE-3
| Pressure Element Material |  | Pressure Element Material |  | SS316L
| Socket Material |  | Socket Material |  | VTS
| Connection Size |  | Connection Size |  | REFER ANNEXURE-3
| Connection Location |  | Connection Location |  | BOTTOM
| Movement Material |  | Movement Material |  | VTS
| Accuracy |  | Accuracy |  | ± 1 % of full scale
| Enclosure Protection Class |  | Enclosure Protection Class |  | IP 55
| Over Range Protection |  | Over Range Protection |  | VTS
| Blow - Out Protection |  | Blow - Out Protection |  | Refer Note-4
| Window Material |  | Window Material |  | SHATTER PROOF GLASS
| Zero Adjustment |  | Zero Adjustment |  | EXTERNAL - REQUIRED
DIAPHRAGM SEAL | Process Connection |  |  |  | REFER ANNEXURE-3
| Diaphragm Material |  | Diaphragm Material |  | Min SS316L
| Bottom Flange Material |  | Bottom Flange Material |  | NA
| Fill Fluid |  | Fill Fluid |  | VTS
| Capillary Length |  | Capillary Length |  | NA
| Capillary Material |  | Capillary Material |  | NA
| Top Flange Material |  | Top Flange Material |  | SS316L
| Flushing Connection |  |  |  | To be provided by Vendor
Wetted Part Material
OPTIONS | Mounting Accessories |  |  |  | REQUIRED
| Pulsation Dampener |  |  |  | Refer Note-2
| Liquid Filled Casing |  |  |  | Refer Note-6
| Syphon Type |  |  |  | VTS
| Syphon Material |  |  |  | VTS
| Stop Pin |  |  |  | REQUIRED
| SS Tag Plate |  |  |  | REQUIRED
CERTIFICATION | Calibration Certificate |  |  |  | REQUIRED
| ATEX Certification |  |  |  | -
PURCHASE | Make |  |  |  | VTS
| Model |  |  |  | VTS
| Qty |  |  |  | 86
| Maintenance Spares |  |  |  | TBA
| Commisioning Spares |  |  |  | VTS
Notes:
1.The gauge for 60 kg/cm2 above pressure shall preferably be a safety type with solid front where pointer and glass are partitioned off from the sensor by a solid disc
2.Pulsation dampeners shall be installed with the gauges where pulsating pressure occurs
3.Bezel rings shall be screw on pattern
4.Blow-out discs are required for all pressure gauges except for instrument air services
5.Vibration proof gauges or remote seal type shall be used if the surrounding environment is subject to vibration
6.Pressure gauges for vibrating services(pump discharge) shall be glycerine filled type or with pulsating dampener device and Sealing liquid must be selected as per process requirement
7.Inbuilt snubber will be provided for diaphragm seal type pressure gauge
8.NA - Not Applicable
VTS- Vendor To Specify

## DS_EXIS WWTP (hidden)
VATECH WABAG LIMITED "WABAG HOUSE" NO.17,200 FEET THORAIPAKKAM PALLAVARAM MAIN ROAD, SUNNAMBU KOLATHUR CHENNAI- 600 117 |  |  |  |  | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR - BOURDON TYPE
PROJECT | SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA |  |  |  | ISSUED FOR |  | ENQUIRY
CLIENT | GAIL
LOCATION | PATA
GENERAL | Tag No |  |  |  | REFER ANNEXURE-4
| P&ID No |  |  |  | REFER ANNEXURE-4
| Location |  |  |  | REFER ANNEXURE-4
| Line No. |  |  |  | REFER ANNEXURE-4
| Area Classification |  |  |  | Safe Area
PROCESS CONDITIONS | Fluid |  |  |  | REFER ANNEXURE-4
| Specific Gravity |  |  |  | REFER ANNEXURE-4
| Viscosity(Centipoise) |  |  |  | REFER ANNEXURE-4
| Flow(m3/hr) | Min. | Nor. | Max. | REFER ANNEXURE-4 | REFER ANNEXURE-4 |  | REFER ANNEXURE-4
| Pressure (Kg/cm2 g) | Min. | Nor. | Max. | REFER ANNEXURE-4 | REFER ANNEXURE-4 |  | REFER ANNEXURE-4
| Temp(°C) | Min. | Nor. | Max. | REFER ANNEXURE-4 | REFER ANNEXURE-4 |  | REFER ANNEXURE-4
SENSOR | Instrument Type |  |  |  | REFER ANNEXURE-4
| Instrument Range |  | Instrument Range |  | REFER ANNEXURE-4
| Mounting |  | Mounting |  | LOCAL
| Dial Size |  | Dial Size |  | 150mm
| Dial Material |  | Dial Material |  | VTS
| Dial Fill Fluid |  | Dial Fill Fluid |  | VTS
| Dial Color |  | Dial Color |  | VTS
| Case |  | Case |  | SS316L
| Bezel Ring |  | Bezel Ring |  | Bayonet Type( Note 3)
| Pressure Element Type |  | Pressure Element Type |  | REFER ANNEXURE-4
| Pressure Element Material |  | Pressure Element Material |  | SS316L
| Socket Material |  | Socket Material |  | VTS
| Connection Size |  | Connection Size |  | REFER ANNEXURE-4
| Connection Location |  | Connection Location |  | BOTTOM
| Movement Material |  | Movement Material |  | VTS
| Accuracy |  | Accuracy |  | ± 1 % of full scale
| Enclosure Protection Class |  | Enclosure Protection Class |  | IP 55
| Over Range Protection |  | Over Range Protection |  | VTS
| Blow - Out Protection |  | Blow - Out Protection |  | Refer Note-4
| Window Material |  | Window Material |  | SHATTER PROOF GLASS
| Zero Adjustment |  | Zero Adjustment |  | EXTERNAL - REQUIRED
DIAPHRAGM SEAL | Process Connection |  |  |  | REFER ANNEXURE-4
| Diaphragm Material |  | Diaphragm Material |  | Min SS316L
| Bottom Flange Material |  | Bottom Flange Material |  | NA
| Fill Fluid |  | Fill Fluid |  | VTS
| Capillary Length |  | Capillary Length |  | NA
| Capillary Material |  | Capillary Material |  | NA
| Top Flange Material |  | Top Flange Material |  | SS316L
| Flushing Connection |  |  |  | To be provided by Vendor
Wetted Part Material
OPTIONS | Mounting Accessories |  |  |  | REQUIRED
| Pulsation Dampener |  |  |  | Refer Note-2
| Liquid Filled Casing |  |  |  | Refer Note-6
| Syphon Type |  |  |  | VTS
| Syphon Material |  |  |  | VTS
| Stop Pin |  |  |  | REQUIRED
| SS Tag Plate |  |  |  | REQUIRED
CERTIFICATION | Calibration Certificate |  |  |  | REQUIRED
| ATEX Certification |  |  |  | -
PURCHASE | Make |  |  |  | VTS
| Model |  |  |  | VTS
| Qty |  |  |  | 20
| Maintenance Spares |  |  |  | TBA
| Commisioning Spares |  |  |  | VTS
Notes:
1.The gauge for 60 kg/cm2 above pressure shall preferably be a safety type with solid front where pointer and glass are partitioned off from the sensor by a solid disc
2.Pulsation dampeners shall be installed with the gauges where pulsating pressure occurs
3.Bezel rings shall be screw on pattern
4.Blow-out discs are required for all pressure gauges except for instrument air services
5.Vibration proof gauges or remote seal type shall be used if the surrounding environment is subject to vibration
6.Pressure gauges for vibrating services(pump discharge) shall be glycerine filled type or with pulsating dampener device and Sealing liquid must be selected as per process requirement
7.Inbuilt snubber will be provided for diaphragm seal type pressure gauge
8.NA - Not Applicable
VTS- Vendor To Specify

## ATTACHMENT 1 (hidden)
Format Number E-05 F / Rev. 0 Attachment 1
WABAG PROJECT No. |  | : | 10P195 |  | IFS PR REF. No. |  | : | 10P195-I0040-24
PROJECT |  | : | SETTING UP OF STORM WATER GUARD ZLD PLANT, NEW WWTP AND AUGMENTATION EXISTING WWTP AT GAIL PATA |  | PR DATE |  | : | 30.07.2025
CLIENT |  | : | GAIL |  | EQPT./ITEM |  | : | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR
LOCATION |  | : | PATA |  | DISCIPLINE |  | : | INSTRUMENTATION
[5 empty] | WABAG PROJECT MANAGER |  | : | MR.MANISH PRUTHI
VENDOR DATA REQUIREMENT (WITH OFFER)
DOCUMENTS REQUIRED WITH THE OFFER:
Sr. no. | Technical Document |  |  | YES / NO | Remarks
1 | No. of offer copies to be submitted |  |  |  | __3__ sets (Hard copies) & Soft copy
2 | Filled and stamped datasheet |  |  |  | Please submit stamped & signed copy of datasheet
3 | Performance curves |  |  |  | Not Applicable
4 | P&I Diagram for the package |  |  |  | Not Applicable
5 |  |  |  |  | If applicable
6 | Compliance statement #
7 | Deviation list #
8 | Technical specs duly signed & stamped |  |  |  | Enquiry Technical specifications
9 | Commissioning Spare parts |  |  |  | Vendor shall recommend
10 | Mandatory Spare parts |  |  |  | if applicable
11 | Recommended Spare parts |  |  |  | Vendor to recommend, if required
12 | Spare parts for O&M |  |  |  | Vendor to provide yearwise spares list for 5 years O&M
13 | Quality assurance plan
14 | Typ. General arrangement drawing
15 | Catalogues and brochures
16 | Reference list for similar models |  |  |  | Vendor to provide reference list for similar application and Local support for the Instrument during O&M
17 | Manufacturing programme
18 | Control Philosophy
19 | Control Architect Drawing- PLC/DCS
20 | Layout Diagram
21 | Sizing Sheet Control valve / Orifice
22 | Overload protection details |  |  |  | if applicable
23 | Wiring diagram
24 | Others (If any) |  |  |  | Vendor to provide
NOTES:
1 | # ' - marked formats are enclosed with the enquiry.

## ATTACHMENT 2 (hidden)
Format Number E-05 F / Rev. 0 Attachment 2
WABAG PROJECT No. |  | : | 10P195 | IFS PR REF. No. | : | 10P195-I0040-24
PROJECT |  | : | SETTING UP OF STORM WATER GUARD ZLD PLANT, NEW WWTP AND AUGMENTATION EXISTING WWTP AT GAIL PATA | PR DATE | : | 30.07.2025
CLIENT |  | : | GAIL | EQPT./ITEM | : | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR
|  |  |  | DISCIPLINE | : | INSTRUMENTATION
|  |  |  | WABAG PROJECT MANAGER | : | MR.MANISH PRUTHI
VENDOR DATA REQUIREMENT (After LOI)
DOCUMENTS REQUIRED AFTER PLACEMENT OF LOI:
S.No. | Technical Document |  |  | Remarks
1 | No. of copies to be submitted |  |  | 3 sets (Hard copies) Within One week on receipt of LOI
2 | Filled up datasheet |  |  | Within One week on receipt of LOI
3 | Performance curves
4 | P&I Diagram for the package
5 | Design calculations |  |  | Within One week on receipt of LOI
6 | Commissioning Spare parts list |  |  | Within One week on receipt of LOI
7 | Mandatory Spare parts |  |  | Within One week on receipt of LOI
8 | Recommended Spare parts list |  |  | Within One week on receipt of LOI
9 | Spare parts list for 5 Yrs O&M |  |  | Within One week on receipt of LOI
10 | Quality assurance plan |  |  | Within One week on receipt of LOI
11 | General arrangement drawing |  |  | Within One week on receipt of LOI
12 | Cross Sectional drawings |  |  | Within One week on receipt of LOI
13 | Catalogues and brochures |  |  | Within One week on receipt of LOI
14 | Reference list for similar models |  |  | Within One week on receipt of LOI
15 | Erection / Assembly drawings with detail BOQ |  |  | Within One week on receipt of LOI
16 | Detailed Manufacturing programme |  |  | Within One week on receipt of LOI
17 | Mgf. Progress report |  |  | Within One week on receipt of LOI
18 | Wiring & Schematic drawing |  |  | Within One week on receipt of LOI
19 | Speed - torque curve
20 | Motor curves
21 | Inspection reports with release notes |  |  | Refer Note 1
22 | Erection, O&M manual |  |  | Within One week on receipt of LOI
23 | Schedule |  |  | Within One week on receipt of LOI
24 | Asbuilt Drawing |  |  | 1 Week before supply
25 | Final Sizing Sheet Control Valve /Orifice
26 | Control Architect Drawing- PLC/DCS
27 | Terminal details / Panel Wiring Detail |  |  | Within One week on receipt of LOI
28 | Calibration and Test Certificates |  |  | Receipt of Material
29 | Warranty certificate |  |  | Receipt of Material
30 | Hazardous / Intrinsic safe approvals
31 | Material Test Certificate |  |  | Receipt of Material
32 | Overload protection |  |  | if applicable
33 | Others (If any) |  |  | Within One week on receipt of LOI, if applicable
NOTES:
1. All the inspection reports shall be complied starting from material identification, in-process inspection to final inspection and release notes issued by client/consultant.

## ATTACHMENT 3 (hidden)
Format Number E-05 F / Rev. 0 Attachment 3
COMPLIANCE STATEMENT (Typical - To be submitted in vendor’s letter head)
| WABAG PROJECT No. |  | : 10P195
| PROJECT |  | : SETTING UP OF STORM WATER GUARD POND, RO ZLD PLANT, NEW WWTP AND AUGMENTATION OF EXISTING WWTP AT GAIL PATA
| EQUIPMENT NAME |  | : | As per Datasheet
| EQUIPMENT TAG NO |  | : | As per Datasheet
We confirm that our offer no:_________________________________ dated :__________ is entirely in compliant to your enquiry ref: no.: ________________________ which comprises of the following Data Sheets
| a | INSTRUMENT DATASHEET FOR
We confirm that no deviation is taken from the above specification,Except points listed in the deviation list. We are attaching herewith the backup papers for justifying the deviation/superiority from the specification. We agree that the deviations are subject to client/consultant approval. If the deviation is not approved by the client, we will adhere to the project specification / datasheet with no time and cost implication.
Name of the Company
Address for Communication
Authorized Signatory
Company name and seal

## ATTACHMENT 4 (hidden)
Format Number E-05 F / Rev. 0 Attachment 4
WABAG PROJECT No. |  | : | 10P195 |  | IFS PR REF. No. |  | : | 10P195-I0040-24
PROJECT |  | : | SETTING UP OF STORM WATER GUARD ZLD PLANT, NEW WWTP AND AUGMENTATION EXISTING WWTP AT GAIL PATA |  | PR DATE |  | : | 30.07.2025
CLIENT |  | : | GAIL |  | EQPT./ITEM |  | : | INSTRUMENT DATASHEET FOR PRESSURE INDICATOR
LOCATION |  | : | PATA |  | DISCIPLINE |  | : | INSTRUMENTATION
[5 empty] | WABAG PROJECT MANAGER |  | : | MR.MANISH PRUTHI
DEVIATION FORMAT
Sl. No. | REFERENCE CLAUSE OF ENQUIRY |  |  | DESCRIPTION OF DEVIATION |  | REASON FOR DEVIATION |  |  | REMARKS

## ATTACHMENT 5 (hidden)
PTR FORMAT
SL.NO | NAME OF PLANT | SUPPLIED MODEL | YEAR OF COMMISSIONING | NAME OF COMPANY/ORGANIZATION | NAME OF CONTACT PERSON | ADDRESS | TELEPHONE NO | FAX NO | E-MAIL ID

## ANNEXURE-2 (hidden)
Format Number E-05 F / Rev. 0 Annexure 2
#REF! |  | : | #REF! |  | #REF! |  | : | #REF!
PROJECT |  | : | #REF! |  | PR DATE |  | : | #REF!
#REF! |  | : | #REF! |  | EQPT./ITEM |  | : | #REF!
[5 empty] | DISCIPLINE |  | : | #REF!
[5 empty] | #REF! |  | : | #REF!
VENDOR DATA REQUIREMENT (WITH OFFER)
DOCUMENTS REQUIRED WITH THE OFFER:
Sr. no. | Technical Document |  |  | YES / NO | Remarks
1 | No. of offer copies to be submitted |  |  |  | __3__ sets (Hard copies) & Soft copy
2 | Filled and stamped datasheet |  |  |  | Please submit stamped & signed copy of datasheet
3 | Performance curves |  |  |  | Not Applicable
4 | P&I Diagram for the package |  |  |  | Not Applicable
5 | Design calculations |  |  |  | If applicable
6 | Compliance statement #
7 | Deviation list #
8 | Technical specs duly signed & stamped |  |  |  | Enquiry Technical specifications
9 | Commissioning Spare parts |  |  |  | Vendor shall recommend
10 | Mandatory Spare parts |  |  |  | if applicable
11 | Recommended Spare parts |  |  |  | Vendor to recommend, if required
12 | Spare parts for O&M |  |  |  | Vendor to provide yearwise spares list for 5 years O&M
13 | Quality assurance plan
14 | Typ. General arrangement drawing
15 | Catalogues and brochures
16 | Reference list for similar models |  |  |  | Vendor to provide reference list for similar application and Local support for the Instrument during O&M
17 | Manufacturing programme
18 | Control Philosophy
19 | Control Architect Drawing- PLC/DCS
20 | Layout Diagram
21 | Sizing Sheet Control valve / Orifice
22 | Overload protection details |  |  |  | if applicable
23 | Wiring diagram
24 | Others (If any) |  |  |  | Vendor to provide
NOTES:
1 | # ' - marked formats are enclosed with the enquiry.
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
No
No
No
No
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No

## ANNEXURE-3 (hidden)
Format Number E-05 F / Rev. 0 Annexure 3
#REF! |  | : | #REF! | #REF! | : | #REF!
PROJECT |  | : | #REF! | PR DATE | : | #REF!
#REF! |  | : | #REF! | EQPT./ITEM | : | #REF!
|  |  |  | DISCIPLINE | : | #REF!
|  |  |  | #REF! | : | #REF!
VENDOR DATA REQUIREMENT (After LOI)
DOCUMENTS REQUIRED AFTER PLACEMENT OF LOI:
S.No. | Technical Document |  |  | Remarks
1 | No. of copies to be submitted |  |  | 3 sets (Hard copies) Within One week on receipt of LOI
2 | Filled up datasheet |  |  | Within One week on receipt of LOI
3 | Performance curves
4 | P&I Diagram for the package
5 | Design calculations |  |  | Within One week on receipt of LOI
6 | Commissioning Spare parts list |  |  | Within One week on receipt of LOI
7 | Mandatory Spare parts |  |  | Within One week on receipt of LOI
8 | Recommended Spare parts list |  |  | Within One week on receipt of LOI
9 | Spare parts list for 5 Yrs O&M |  |  | Within One week on receipt of LOI
10 | Quality assurance plan |  |  | Within One week on receipt of LOI
11 | General arrangement drawing |  |  | Within One week on receipt of LOI
12 | Cross Sectional drawings |  |  | Within One week on receipt of LOI
13 | Catalogues and brochures |  |  | Within One week on receipt of LOI
14 | Reference list for similar models |  |  | Within One week on receipt of LOI
15 | Erection / Assembly drawings with detail BOQ |  |  | Within One week on receipt of LOI
16 | Detailed Manufacturing programme |  |  | Within One week on receipt of LOI
17 | Mgf. Progress report |  |  | Within One week on receipt of LOI
18 | Wiring & Schematic drawing |  |  | Within One week on receipt of LOI
19 | Speed - torque curve
20 | Motor curves
21 | Inspection reports with release notes |  |  | Refer Note 1
22 | Erection, O&M manual |  |  | Within One week on receipt of LOI
23 | Schedule |  |  | Within One week on receipt of LOI
24 | Asbuilt Drawing |  |  | 1 Week before supply
25 | Final Sizing Sheet Control Valve /Orifice
26 | Control Architect Drawing- PLC/DCS
27 | Terminal details / Panel Wiring Detail |  |  | Within One week on receipt of LOI
28 | Calibration and Test Certificates |  |  | Receipt of Material
29 | Warranty certificate |  |  | Receipt of Material
30 | Hazardous / Intrinsic safe approvals |  |  | As per the requirement
31 | Material Test Certificate |  |  | Receipt of Material
32 | Overload protection |  |  | if applicable
33 | Others (If any) |  |  | Within One week on receipt of LOI, if applicable
34 | 3D Model of the Instrument |  |  | Within One week on receipt of LOI
NOTES:
1. All the inspection reports shall be complied starting from material identification, in-process inspection to final inspection and release notes issued by client/consultant.
Yes
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
Yes
No
No
Yes
No
Yes
No
Yes
No
No
No
No
Yes
No
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
No
Yes
No

## ANNEXURE-4 (hidden)
Format Number E-05 F / Rev. 0 Annexure 4
COMPLIANCE STATEMENT (Typical - To be submitted in vendor’s letter head)
| #REF! |  | : | #REF!
| #REF! |  | : | #REF!
| EQUIPMENT NAME |  | : | As per Datasheet
| EQUIPMENT TAG NO |  | : | As per Datasheet
We confirm that our offer no:_________________________________ dated :__________ is entirely in compliant to your enquiry ref: no.: ________________________ which comprises of the following Data Sheets
| a | #REF!
We confirm that no deviation is taken from the above specification,Except points listed in the deviation list. We are attaching herewith the backup papers for justifying the deviation/superiority from the specification. We agree that the deviations are subject to client/consultant approval. If the deviation is not approved by the client, we will adhere to the project specification / datasheet with no time and cost implication.
Name of the Company
Address for Communication
Authorized Signatory
Company name and seal

## ANNEXURE-5 (hidden)
Format Number E-05 F / Rev. 0 Annexure 5
#REF! |  | : | #REF! |  | #REF! |  | : | #REF!
#REF! |  | : | #REF! |  | PR DATE |  | : | #REF!
#REF! |  | : | #REF! |  | EQPT./ITEM |  | : | #REF!
[5 empty] | DISCIPLINE |  | : | #REF!
[5 empty] | #REF! |  | : | #REF!
DEVIATION FORMAT
Sl. No. | REFERENCE CLAUSE OF ENQUIRY |  |  | DESCRIPTION OF DEVIATION |  | REASON FOR DEVIATION |  |  | REMARKS

## ANNEXURE-6 (hidden)
PTR FORMAT
SL.NO | NAME OF PLANT | SUPPLIED MODEL | YEAR OF COMMISSIONING | NAME OF COMPANY/ORGANIZATION | NAME OF CONTACT PERSON | ADDRESS | TELEPHONE NO | FAX NO | E-MAIL ID

## ANNEXURE-7 (hidden)
INSTRUMENT SPCIFICATION AS PER CONTRACT |  | VENDOR REPLY
S.NO | GENERAL REQUIREMENT
1 | Instrument shall be calibrated and their accuracy verified at a minimum of five rising/falling points (0%, 25%, 50%, 75% and 100%). All calibrations shall be recorded on ISA format calibration sheets.
S.NO | SPECIFICATION AS PER CONTRACT
1 | As attached

## ANNEXURE-8 (hidden)
VA TECH WABAG
Wabag House, #17, 200 Feet Radial Road
S. Kolathur, Chennai – 600 117 Tamil Nadu, India
Format Number E-05 F / Rev. 0
VARIANCE ANALYSIS ( ANNEXURE-8)
PROJECT No. |  | 10P169 |  |  | PR REF. No. | #REF! | DATE | #REF!
PROJECT |  | DESIGN BUILD & OPERATE (DBO) CONTRACT FOR RECONSTRUCTION, EXPANSION, OPERATION OF PAGLA STP |  |  | EQPT./ITEM | FLOW INDICATING TRANMISTTER - ELECTROMAGNETIC TYPE
LOCATION |  | PAGLA, BANGLADESH |  |  | DISCIPLINE | INSTRUMENTATION
CLIENT |  | DHAKA WATER SUPPLY & SEWERAGE AUTHORITY (DWASA) |  |  | PROJECT MANAGER | MR. SANTOSH PRAKASH GUND, MR. ARVINDRATNAM N
Sl. No. | MAME OF THE INSTRUMENT |  | PROPOSAL STAGE |  | DETAILED ENGINEERING |  |  | Remarks
Sl. No. |  |  | SPECIFICATION | QTY | SPECIFICATION |  | Qty
1 | FLOW INDICATING TRANMISTTER - ELECTROMAGNETIC TYPE |  | - | 15 | As per Datasheet |  | 23 | Variance
[5 empty] | Total |  | 23
Reason for Variance:
During Proposal stage 1 no. of Wetwell Flow measurement is condiered as Flowmeter (Electromagnetic type) but as per P&ID Rev.B 2 nos of Ultraonic flowmeter is provided. Various discussion with the Vendor for Ultrasonic flowmeter was conducted and concluded that straight length is not available for Parshall flume and accuracy is less for Area velocity flowmeter. Hence in line with Process Dept confirmation it was concluded to provide Electromagnetic flowmeter in Individual discharge of the Wet well pumps.(Regarding the same mail has ben attached). Due to this 7Nos Flowmeter (Electromagnetic type) is added and for RAS Pump Discharge Only 2nos Flowmeter (Electromagnetic type) considered during proposal now its 4Nos. and for Hot water recirculation Pumps DPT type flow transmitter considered during Proposal.
Proposal |  |  | Engineering |  | Engineering |  | #REF!
Deepan Chakravarthy G |  |  | Sudhagar R |  | Karthikeyan S
Signature |  |  | Discipline Engineer |  | Technical Co-ordinator |  | Date